## Rev
Revision History
Date | Revision | Author | Description of Changes | Notes
46099 | 1 | ABartholomaus | Original Revision
46142 | 1.1 | ABartholomaus | Added Rev History Added Firmware revision column for hardware sheets Modified formatting on all sheets for consistency

## Checklist
Task | Required | Completed | Notes
PLC Program Backup | TRUE | FALSE
HMI Program Backup | TRUE | FALSE
SCADA Backup | FALSE | FALSE
RSNetworx Backup (CNet, DNet) | TRUE | FALSE
DH+/RIO Backup | TRUE | FALSE
Existing Plant Drawings | TRUE | FALSE
Existing Network Diagram | TRUE | FALSE
Process Flow Diagram | TRUE | FALSE
Process Investigation | FALSE | FALSE
Operator Interviews | TRUE | FALSE
IO List | TRUE | FALSE
Device List | TRUE | FALSE
Panel Sheet | TRUE | TRUE
Power Sheet | TRUE | TRUE
PLC Racks Sheet | TRUE | TRUE
PLC Slots sheet | TRUE | TRUE
HMIs Sheet | TRUE | TRUE
Ethernet Switches Sheet | TRUE | TRUE
Switch Ports Sheet | TRUE | FALSE
Fieldbus IO Sheet | TRUE | TRUE
Devices Sheet | TRUE | TRUE
Conv. Speeds Sheet | FALSE | TRUE
Safety Circuit Sheet | TRUE | TRUE
Safety Devices Sheet | TRUE | TRUE
Peer to Peer Comms | TRUE | TRUE

## Panels
General Data | [5 empty] | Nameplate Data | [5 empty] | External Panel Measurements (Inches) |  |  |  | External Clearance (Inches) | [5 empty] | Photo Checklist
Folder Hyperlink | Area | Panel Name | Description | Panel Location | Power Feed Circuit | Phase | FLA | Volts Max | SCC | Frequency | Largest Motor HP | Height | Width | Depth | Legs | Top | Bottom | Left | Right | Front | Back | Panel Labels | Full Panel | Each Door | Each Section | Transformers | Power Supplies | Power Disribution | Fuses/CBs | HMIs | VFDs | Motor Starters | PLC Rack | Safety Relay | Misc. Control Hardware
Photos/MCC PLC Cabinet #1/Panels/MCC PLC Cabinet #1/ | MCC Room | MCC PLC Cabinet #1 | Main ControlLogix processor + Ethernet bridge cabinet | MCC Room, north wall | MCC-Main-CB1 | Single | 5 | 120 |  | 60 | N/A | 72" | 36" | 12"
Photos/MCC-0025/Panels/MCC-0025/ | E & F Cookers | MCC-0025 | Drive cabinet for E/V Coolers (PF40 ×2) | Behind Cooker F Infeed | MCC-54C-2B | Three |  | 480 | 5.39kA | 60 | 10 | 95 7/8" | 179 1/2" | 37 5/8"
Photos/IDF B/Panels/IDF B/ | War Room | IDF B | Network distribution cabinet (managed switch + patch panel) | War Room SE corner |  | Single |  | 120 |  | 60
Note on G1: Austin Bartholomaus: Document all of the information listed on the panel nameplate, if there is not a nameplate look for existing drawings that list the information
Note on A2: Austin Bartholomaus: Hyperlink to the folder containing all of the panel pictures and documentation
Note on B2: Austin Bartholomaus: What area of the plant is the panel located in?
Note on C2: Austin Bartholomaus: What is the name of the panel? Make sure this aligns with how the panel is labeled in the field.
Note on D2: Austin Bartholomaus: If the panel label does not match what the plant calls the panel, make sure to list the plants reference here
Note on E2: Austin Bartholomaus: Describe how to locate the panel if someone else were to go looking for it i.e. on the north side of the filler
Note on F2: Austin Bartholomaus: What distribution panel/MCC bucket/etc. is the panel fed from?

## Power
General Data | [6 empty] | Outgoing/Output Power |  |  |  |  | Incoming/Input Power | [5 empty] | Photo Checklist
Photo Hyperlink | Area | Panel Name | Drawing Reference | Device Name | Part Number | Safety Circuit | Voltage Out | Amperage Out | Phase Out | Wire Number (V+ Out) | Wire Number (COM Out) | Voltage In | Amperage In | Phase In | Fuse/CB # | Wire Number (V+) | Wire Number (COM) | Device | Location | PS Part Number | Wire Numbers
Photos/MCC PLC Cabinet #1/Power/MCC PLC Cabinet #1/ | MCC Room | MCC PLC Cabinet #1 | DWG-MCC-001 sheet 3 |  |  |  | 120 VAC |  | Single |  |  | 120 VAC |  | Single |  | L1 | N
Photos/MCC-0025/Power/MCC-0025/ | E & F Cookers | MCC-0025 | DWG-MCC-0025 sheet 1 |  |  |  | 120 VAC | 10 | Single |  |  | 480 VAC | 30 | Three
Photos/MCC-0025/Power/PS-24V-Bus1/ | E & F Cookers | MCC-0025 |  | PS-24V-Bus1 | APS-DR1072-24 |  | 24 VDC | 5 | N/A |  |  | 120 VAC |  | Single
Note on A2: Austin Bartholomaus: Hyperlink to the photo of the power device
Note on B2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.
Note on C2: Austin Bartholomaus: Name of the panel. This should match the panel name listed on the panel sheet
Note on D2: Austin Bartholomaus: Sheet-Line-Instance reference to the device in existing drawing sets.
Note on E2: Austin Bartholomaus: Device Name/Label as it appears in the drawing sets OR how it is labeled in the field.
Note on G2: Austin Bartholomaus: Safety Circuit that this power device is associated with. This should match the Safety Circuit name from the Safety Circuit sheet.

## PLC Racks
General Data | [9 empty] | Chassis Power |  |  |  |  | Measurements (Inches) |  |  | Clearance (Inches) | [5 empty] | Photo Checklist
Folder Hyperlink | IO List Completed | Area | Panel Name | Rack Name | Description | Part Number | Comm Address (IP, Serial, Fieldbus, RIO) | Comm Protocol | Comm Wire Number | Power Supply Part Number | Voltage | Wire Number (V+) | Wire Number (COM) | Fuse/CB | Height | Width | Depth | Top | Bottom | Left | Right | Front | Back | Full Rack | Power Feed | Part Numbers | Comm Cabling (Wire Numbers) | Wire Numbers
Photos/MCC PLC Cabinet #1/PLC Racks/Local/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | Main MCC ControlLogix rack | 1756-A10 | 172.25.106.100 | EtherNet/IP |  | 1756-PA75 | 120 VAC | L1 | N | CB-MCC-1
Photos/MCC-0025/PLC Racks/MCC-0025 Flex/ | FALSE | E & F Cookers | MCC-0025 | MCC-0025 Flex | Remote FlexLogix bank for cooker drive enables and door interlocks | 1794-AENT | 172.25.106.115 | EtherNet/IP | ETH-115 | 1794-PS13 | 24 VDC | DC+ | DC- | F-0025-1
Note on A2: Austin Bartholomaus: Hyperlink to the folder containing all of the panel pictures and documentation
Note on B2: Austin Bartholomaus: Has the IO list been completed for this item? This includes getting all slots, wire numbers, field wiring, scaling, etc.
Note on C2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.
Note on D2: Austin Bartholomaus: Name of the panel. This should match the panel name listed on the panel sheet

## PLC Slots
General Data | [8 empty] | Power Bus 1 | [6 empty] | Power Bus 2 | [6 empty] | Photo Checklist
Photo Hyperlink | IO List Completed | Area | Panel Name | Rack Name | Description | Part Number | Firmware Revision | Slot | Safety Circuit | Voltage | IO Terminal (V+) | Wire Number (V+) | IO Terminal (COM) | Wire Number (COM) | Fuse/CB | Safety Circuit 2 | Voltage 2 | IO Terminal 2 (V+) | Wire Number 2 (V+) | IO Terminal 2 (COM) | Wire Number 2 (COM) | Fuse/CB 2 | Slot Part Number | Location | Card/Field Wiring | Wire Numbers
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 0 · 1756-L72/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | MCC Processor | 1756-L72 | 32.013 | 0
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 1 · 1756-EN2T/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | EtherNet/IP Bridge | 1756-EN2T | 11.001 | 1
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 2 · 1756-N2/ |  | MCC Room | MCC PLC Cabinet #1 | Local | SPARE | 1756-N2 |  | 2
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 3 · 1756-IB16/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | 16-pt 24VDC Sink Input | 1756-IB16 | 3.001 | 3 |  | 24 VDC | 0-15 | I-301..I-316 |  |  | CB-MCC-3
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 4 · 1756-OB16/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | 16-pt 24VDC Source Output | 1756-OB16 | 3.001 | 4 |  | 24 VDC | 0-15 | O-401..O-416 |  |  | CB-MCC-4
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 5 · 1756-OW16I/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | 8-pt 24VDC Isolated Relay Output | 1756-OW16I | 2.001 | 5 |  | 24 VDC | 0-15 | O-501..O-516 |  |  | CB-MCC-5
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 6 · 1756-IF8I/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | 8-ch Isolated Analog Input (4-20mA) | 1756-IF8I | 3.002 | 6 |  | 24 VDC | Ch0+..Ch7+ | AI-601..AI-608 |  |  | CB-MCC-6
Photos/MCC PLC Cabinet #1/PLC Slots/Slot 7 · 1756-OF4/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Local | 4-ch Isolated Analog Output (4-20mA) | 1756-OF4 | 3.002 | 7 |  | 24 VDC | Ch0+..Ch3+ | AO-701..AO-704 |  |  | CB-MCC-7
Note on C2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.
Note on D2: Austin Bartholomaus: Name of the panel. This should match the panel name listed on the panel sheet

## Fieldbus IO
General Data | [10 empty] | Power Bus #1 (Duplicate if multiple power buses) | [5 empty] | Relative Distance (Feet) | [5 empty] | Measurements (Inches) |  |  | Clearance (Inches) | [5 empty] | Photo Checklist
Photo Hyperlink | IO List Completed | Area | Panel Name | Device Name | Description | Part Number | Firmware Revision | Comm Address (IP, Serial, Fieldbus, RIO) | Comm Protocol | Comm Wire Number | Power Supply | Source Panel | Voltage | Wire Number (V+) | Wire Number (COM) | Fuse/CB | Nearest Panel | Nearest Fieldbus IO 1 | Nearest Fieldbus IO 1 Name | Nearest Fieldbus IO 2 | Nearest Fieldbus IO 2 Name | Nearest Power Source | Height | Width | Depth | Top | Bottom | Left | Right | Front | Back | Field Device | Field Device Location | Field Device Part Number | Comm Cabling (Wire Number) | Wire Numbers
Photos/MCC-0025/Fieldbus IO/Cooker E POINT IO/ | FALSE | E & F Cookers | MCC-0025 | Cooker E POINT IO | POINT IO drop on Cooker E framework — drive run/stop + door interlock | 1734-AENT | 5.012 | 172.25.106.116 | EtherNet/IP | ETH-116 | MCC-0025 internal 24VDC bus | MCC-0025 | 24 VDC | DC+ | DC- | F-0025-2 | MCC-0025 | [14 empty] | Cooker E run permissive + interlock proximity switches | Cooker E framework, near drive #1
Photos/MCC-0025/Fieldbus IO/Cooker V POINT IO/ | FALSE | E & F Cookers | MCC-0025 | Cooker V POINT IO | POINT IO drop on Cooker V framework — same role as Cooker E drop | 1734-AENT | 5.012 | 172.25.106.117 | EtherNet/IP | ETH-117 | MCC-0025 internal 24VDC bus | MCC-0025 | 24 VDC | DC+ | DC- | F-0025-3 | MCC-0025 | [14 empty] | Cooker V run permissive + door interlock proximity switches | Cooker V framework, mid deck
Note on C2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.
Note on D2: Austin Bartholomaus: Name of the panel in which the communication bus is terminated/controlled. This should match the panel name listed on the panel sheet

## Network Devices
Devices include but are not limited to: VFDs, SoftStarts, analytical sensors, flow meters, power monitors, etc. | [11 empty] | Panel Power must be verified off before taking these measurements
General Data | [11 empty] | Control Device Measurements (Inches) |  |  | Control Device Clearance (Inches) | [5 empty] | Photo Checklist
Photo Hyperlink | Device List Completed | Area | Panel Name | Device Name | Description | Part Number | Firmware Revision | Comm Address (IP, Serial, Fieldbus, RIO) | Communication Protocol | Comm Wire Number | Safety Circuit | Height | Width | Depth | Top | Bottom | Left | Right | Front | Back | Control Device (VFD, MS, Relay, IO Card) | Control Device Wiring | Control Device Comm Cable (Wire Number) | Field Device (Motor, valve, flowmeter, etc.) | Field Device Location/Area | Field Device Nameplate | Field Device Part Number | Field Device Wiring
Photos/MCC-0025/Network Devices/E Cooler/ | TRUE | E & F Cookers | MCC-0025 | E Cooler | PowerFlex 40 — 10HP, drives E Cooler conveyor | 22B-D017N104 | 5.001 | 172.25.106.110 | EtherNet/IP | [11 empty] | VFD |  |  | 10HP TEFC motor | E Cooler upper deck
Photos/MCC-0025/Network Devices/V Cooler/ | TRUE | E & F Cookers | MCC-0025 | V Cooler | PowerFlex 40 — 7.5HP, drives V Cooler conveyor | 22B-D012N104 | 5.001 | 172.25.106.111 | EtherNet/IP | [11 empty] | VFD |  |  | 7.5HP TEFC motor | V Cooler middle gear
Photos/IDF B/Network Devices/AP-WarRoom-1/ | TRUE | War Room | IDF B | AP-WarRoom-1 | Plant Wi-Fi access point — operator tablets | AIR-AP1815I-B-K9 | 17.9.4 | 10.226.40.45 | EtherNet/IP | [11 empty] | N/A |  |  | N/A | War Room ceiling, NE corner
Note on C3: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.
Note on D3: Austin Bartholomaus: Name of the panel where the device resides. This should match the panel name listed on the panel sheet

## HMIs
General Data | [11 empty] | Power |  |  |  |  | Cut Out Measurement (Inches) |  | Measurements (Inches) |  |  | Clearance (Inches) | [5 empty] | Photo Checklist
Folder Hyperlink | Program Uploaded | Area | Panel Name | HMI Name | Application Name | Description | Hardware Platform | Firmware Revision | Comm Address (IP, Serial, Fieldbus, RIO) | Comm Protocol | Comm Wire Number | Power Supply Part Number | Voltage | Wire Number (V+) | Wire Number (COM) | Fuse/CB | Height | Width | Height 2 | Width 2 | Depth 2 | Top | Bottom | Left | Right | Front | Back | Full HMI (Front/Back) | Power Feed | Part Numbers (Screen/Logic Module) | Comm Cabling (Wire Number) | Wire Numbers
Photos/MCC PLC Cabinet #1/HMIs/Gallon_Cookers/ | TRUE | MCC Room | MCC PLC Cabinet #1 | Gallon_Cookers | Gallon_Cookers_v3.2 | Cookers/Coolers 7-9 + E/V cookers operator interface | WonderWare InTouch | 2020 R2 | 10.226.40.19 | EtherNet/IP |  | APS-DR1072-24 | 24 VDC |  |  |  | 14 1/4" | 12"
Photos/MCC-0025/HMIs/Cooker_Local/ | FALSE | E & F Cookers | MCC-0025 | Cooker_Local | Cooker_Local_v1.0 | Local cooker drive operator interface (door-mount) | PanelView Plus 600 | 11.001 | 172.25.106.112 | EtherNet/IP | ETH-112 | APS-DR1072-24 | 24 VDC | DC+ | DC- | F-0025-4 | 9 1/2" | 12"
Note on C2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.
Note on D2: Austin Bartholomaus: Name of the panel where the device resides. This should match the panel name listed on the panel sheet

## Ethernet Switches
General Data | [7 empty] | Power |  |  |  |  | Clearance (Inches) | [5 empty] | Photo Checklist
Folder Hyperlink | Configuration Backup | Network Investigation Complete | Area | Panel Name | Name | Part Number | # Ports in use | Power Supply | Voltage | Wire Number (V+) | Wire Number (COM) | Fuse/CB | Top | Bottom | Left | Right | Front | Back | Device | Power Wiring | Comm Cable Wire Numbers
Photos/MCC PLC Cabinet #1/Ethernet Switches/N-TRON/ | TRUE | TRUE | MCC Room | MCC PLC Cabinet #1 | N-TRON | 516TX-A | 10 | 120VAC -> 24VDC | 24 VDC | L+ | L- | N/A (First in Group) | 5 7/8" | 4 3/4" | 1 1/4"
Photos/IDF B/Ethernet Switches/B3/ | TRUE | TRUE | War Room | IDF B | B3 | Stratix 5700 (1783-BMS10CGN) | 8 | 120VAC -> 24VDC | 24 VDC | L+ | L-
Note on D2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.
Note on E2: Austin Bartholomaus: Name of the panel where the device resides. This should match the panel name listed on the panel sheet

## Drive Parameters
General Data |  |  | Parameters (**Add as many as are needed)
Area | Panel Name | Device Name | Motor NP Volts | Motor NP Hz | Motor NP RPM | Motor NP Power (HP/kW) | Motor OL Current | Minimum Freq. | Maximum Freq. | Start Mode | Stop Mode | Speed Reference | Accel Time 1 (sec) | Decel Time 1 (sec) | Digital In1 | Digital In2 | Digital In3 | Relay Out1 | Relay Out2
E & F Cookers | MCC-0025 | E Cooler | 460 | 60 |  |  | 12 | 0 | 100 | 2-Wire | Ramp, CF | InternalFreq (60Hz) | 10 | 0.5
E & F Cookers | MCC-0025 | V Cooler | 460 | 60 |  |  | 12 | 0 | 100 | 2-Wire | Coast, CF | Drive Pot | 10 | 5
Note on A2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.

## Conv. Speeds
General Data |  | Speed 1 |  | Speed 2 |  | Speed 3 |  | Speed 4 |  | Speed 5
Area | Device Name | Tach Reading 1 (fpm) | VFD Speed 1 (Hz) | Tach Reading 2 (fpm) | VFD Speed 2 (Hz) | Tach Reading 3 (fpm) | VFD Speed 3 (Hz) | Tach Reading 4 (fpm) | VFD Speed 4 (Hz) | Tach Reading 5 (fpm) | VFD Speed 5 (Hz)
E & F Cookers | E Cooler | 6.4 | 60
E & F Cookers | V Cooler | 27.1 | 62.1
Note on A2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.

## Safety Circuit
General Data | [9 empty] | Photo Checklist
Photo Hyperlink | Area | Panel Name | Drawing Reference | Circuit Name | Description | Circuit Rating | MSR Part Number | Input Device Count | Output Device Count | Device | Location | Part Number | Wire Numbers
Photos/MCC-0025/Safety Circuit/MCR/ | E & F Cookers | MCC-0025 | DWG-SAFETY-MCC-0025 | MCR | Master Control Relay — drops drive enables on E-Stop or guard interlock open | 6A | 440R-N23132 (Cutler-Hammer aux) | 3 | 2
Photos/MCC-0025/Safety Circuit/Guard Doors/ | E & F Cookers | MCC-0025 | DWG-SAFETY-MCC-0025 | Guard Doors | Guard door interlock — drops drive run permissive on any cooker access door open | 4A | 440R-D22R2 | 4 | 1
Note on B2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.

## Safety Devices
General Data | [11 empty] | Photo Checklist
Photo Hyperlink | Area | Panel Name | Safety Circuit | Drawing Reference | Device Name | Description | Part Number | Safety Input Count (To PLC/MSR) | Safety Input Wire Numbers | Safety Output Count (From PLC/MSR) | Safety Ouput Wire Numbers | Device | Location | Device Part Number | Wire Numbers
Photos/MCC-0025/Safety Devices/E-Stop Cooker E/ | E & F Cookers | MCC-0025 | MCR | DWG-SAFETY-MCC-0025 | E-Stop Cooker E | Mushroom E-Stop on Cooker E operator station | 800FP-MT44 (red mushroom, 22mm, NC×2) | 2 | S-101, S-102
Photos/MCC-0025/Safety Devices/E-Stop Cooker V/ | E & F Cookers | MCC-0025 | MCR | DWG-SAFETY-MCC-0025 | E-Stop Cooker V | Mushroom E-Stop on Cooker V operator station | 800FP-MT44 (red mushroom, 22mm, NC×2) | 2 | S-103, S-104
Photos/MCC-0025/Safety Devices/Guard Door Cooker E (West)/ | E & F Cookers | MCC-0025 | Guard Doors | DWG-SAFETY-MCC-0025 | Guard Door Cooker E (West) | Tongue-actuated guard switch on Cooker E west access door | 440K-T11090 (Trojan T15) | 2 | S-201, S-202
Photos/MCC-0025/Safety Devices/Guard Door Cooker V (West)/ | E & F Cookers | MCC-0025 | Guard Doors | DWG-SAFETY-MCC-0025 | Guard Door Cooker V (West) | Tongue-actuated guard switch on Cooker V west access door | 440K-T11090 (Trojan T15) | 2 | S-203, S-204
Note on B2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.

## Peer to Peer Comms
General Data | [5 empty] | Message
Area | Device Name | Description | Hardware Platform/Part Number | Comm Address (IP, Serial, Fieldbus, RIO) | Communication Protocol | Type | Source Tag | Destination Device Name | Destination Part Number | Destination Address | Destination Tag | Communication Path
MCC Room | MCC L72 | Cooler #1 fault status pull from old gallon PLC | 1756-L72 | 172.25.106.100 | EtherNet/IP | MSG — CIP Generic Read | Cooler_1_Fault_MSG | Old_Gallon_PLC |  | 172.25.106.50 | Cooler_1_DriveData | 1, 4, 2, 9
MCC Room | MCC L72 | Live oven temperature push to Plant SCADA gateway | 1756-L72 | 172.25.106.100 | EtherNet/IP | MSG — CIP Generic Write | Cooker_Temps_Push | Plant_SCADA_GW |  | 10.226.40.5 | Cooker_TempArray | 1, 4, 2, 5
Note on A2: Austin Bartholomaus: Area where the panel is located, copied from the Panel sheet.

## Notes
Job Notes
Sample investigation seeded on first launch. Three panels (MCC PLC Cabinet #1, MCC-0025, IDF B) with cross-referenced PLC, drive, network, and safety entries. Delete this job anytime; you can re-seed it from Settings → Reload sample job.
Sheet | Panel | Row | Notes
Panels | MCC PLC Cabinet #1 | (sheet) | Cabinet was installed during 2014 line build. Door interlock is operational. No labels on inside of door — recommend label kit during next outage.
Panels | MCC PLC Cabinet #1 | MCC PLC Cabinet #1 | Verified door swing clearance is adequate.
Panels | MCC-0025 | MCC-0025 | Front access tight — 28" clearance to opposite wall.
Power | MCC-0025 | MCC-0025 | Incoming 480V from MCC-54C-2B per drawing.
PLC Racks | MCC PLC Cabinet #1 | Local | 10-slot chassis, all slots populated except 2.
PLC Racks | MCC-0025 | MCC-0025 Flex | 8-slot terminal base; status LED green at investigation.
PLC Slots | MCC PLC Cabinet #1 | Slot 2 · 1756-N2 | Empty filler.
PLC Slots | MCC PLC Cabinet #1 | Slot 5 · 1756-OW16I | Drives MCR drop coils for downstream MCCs.
PLC Slots | MCC PLC Cabinet #1 | Slot 6 · 1756-IF8I | Cooker zone temperatures + product flow.
PLC Slots | MCC PLC Cabinet #1 | Slot 7 · 1756-OF4 | Burner gas valve setpoints (zones 1-4).
Fieldbus IO | MCC-0025 | Cooker E POINT IO | 1×1734-IB8, 1×1734-OB8E populated.
Fieldbus IO | MCC-0025 | Cooker V POINT IO | Same configuration as Cooker E POINT IO.
Network Devices | MCC-0025 | E Cooler | Drive is OEM original (2014 install).
Network Devices | IDF B | AP-WarRoom-1 | PoE-fed from B3 port G3.
HMIs | MCC PLC Cabinet #1 | Gallon_Cookers | Industrial PC behind cabinet door.
HMIs | MCC-0025 | Cooker_Local | Door-mount; runtime backup not on file. Application authored 2018.
Ethernet Switches | IDF B | B3 | Uplink to plant core via fiber port G1.
Drive Parameters | MCC-0025 | (sheet) | Both drives are factory PowerFlex 40s; configuration matches OEM. Recommend dropping decel on V Cooler to 1s during next mod.
Safety Circuit | MCC-0025 | MCR | Existing Cutler-Hammer relay; recommend MSR replacement next outage.
Safety Circuit | MCC-0025 | Guard Doors | Circuit drops MCR via aux contact; drives stop on coast.
Peer to Peer Comms | MCC PLC Cabinet #1 | MCC L72 | 1-second push interval; uses unconnected message buffer.